# Project AF2-424 – Short-Circuit Study Assumptions Used

| ID | Assumption | Basis / Reason | Impact on Study | Status |
| --- | --- | --- | --- | --- |
| A-01 | Pre-fault system voltage is assumed at nominal unless otherwise noted. | Used as the default starting point for fault calculations. | Affects calculated available fault current magnitude. | Open |
| A-02 | Transmission Owner / Area Number for AF2-424 was inferred as PPL (Area 229) based on the POI location (Reed / Reed Tap #1 substations, Northumberland County, PA); PJM Serial Service was not accessible to confirm the TO directly. | Northumberland County, PA falls within PPL Electric Utilities' service territory per public utility service-area records. | If incorrect, the wrong OSF file and area number would be applied in ASPEN, invalidating the short-circuit ratings check. | Open - confirm TO/area number via PJM Serial Service before running the case. |
| A-03 | GSU (AF2-424_inx1 / AF2-424_inv1) low-side winding grounding was not specified in the QP data (listed only as "Wye"); Ungrounded Wye was assumed. | Typical practice for inverter-coupled pad-mount GSUs, consistent with precedent from prior projects. | Affects the zero-sequence fault current path/magnitude at the inverter terminal bus. | Open - confirm against GSU nameplate/datasheet if available. |
| A-04 | MPT (AF2-424_mn / AF2-424_inxc) zero-sequence reactance: QP data lists X0 = 0.06604 pu (R0 = 0.001622 pu), but a PJM deficiency comment on the QP notes the FAT report value is Z0 = 0.0692 pu and states the FAT value will be used. The FAT report was not provided, so the QP table value was used in this study. | QP deficiency comment references a FAT report not included in the uploaded package. | Understates zero-sequence MPT impedance if the FAT value should govern; affects ground fault duty on the 69 kV side. | Open - obtain FAT report and update MPT zero-sequence impedance if it differs from the QP value. |
| A-05 | POI connection is a line tap ("Reed" to "Reed Tap #1", 69 kV) with QP-stated distances of 0.85 mi (to Reed) and 7.01 mi (to Reed Tap #1). Whether the existing Reed-Reed Tap #1 line in the base OneLiner case matches these distances could not be verified without ASPEN OneLiner access. | ASPEN OneLiner is not available in this environment; base case could not be opened. | Per procedure, tap-point placement and any length-proportional impedance scaling must be confirmed against the base case before applying the change file. | Open - verify tap line length/impedance in ASPEN OneLiner per handoff notes. |
| A-06 | This package models the AF2-424 queue only. QP comments state AF2-424 and AF2-425 share a POI and are jointly studied to a combined 40 MW AC facility, but no AF2-425-specific package was provided. | Only the AF2-424 QP data and SLD were provided; no AF2-425 data was uploaded. | If AF2-425 requires separate or combined modeling, this study may need to be revised. | Open - confirm with project owner whether AF2-425 needs its own or a combined short circuit study. |